## Risk Ranking
Team members: Adrian Everingham & Stephen Bushell |  |  | Date created for this workplace: 09/02/2016 |  | Date of This Revision: 12/02/2024 | Workplace: 255 Elizabeth Street, Sydney (LA2005) | [5 empty] | Division: LAT Portfolio
Current Revision: F
LIKELIHOOD (L) |  |  | CONSEQUENCE (C) - IMPACT |  |  | RISK RANKING (R) | [5 empty] | Risk Ranking Summary
[7 empty] | 1 | 2 | 3 | 4 | 5 | EXTREME-These risks are Unacceptable. The work activity should be halted until Critical Controls are implemented which reduce the risk to no greater than High. If it is not possible to reduce the risk, the work should remain prohibited.
A | Almost Certain | Expected to be the outcome in most cases - 91 - 100% probable | 1 | Insignificant | First aid injury/s (FAI), minor environmental impact. Minor/ medium term social impacts on local population, or expected financial impact = < $10k. | A | M (8) | M (13) | H (18) | E (23) | E (25)
B | Likely | Will probably occur in most circumstances - 51 - 90% probable | 2 | Minor | Medical Treatment Injury (MTI), minor short term environmental impact. Attention from media & heightened concern by local community or expected financial impact = $10k - $100k. | B | M (7) | M (12) | H (17) | H (21) | E (24) | HIGH-These risks must be reduced where possible by implementing higher levels of Critical Control using the Hierarchy of Controls. Where the residual risk is not able to be reduced lower than High, a controlled work methodology must be in place and reviewed by the HSE Lead and Workplace Manager.
C | Possible | Might occur some time 31 - 50% probable | 3 | Moderate | Lost Time Injury (LTI). Serious irreversible injury/disease, serious medium term environmental harm. Adverse local media coverage, or expected financial impact = $100k - $1 mill. | C | L (4) | M (11) | H (16) | H (20) | H (22) | MEDIUM-Identified Critical Controls must be capable of reducing the risk by eliminating or minimising to an acceptable level. # Critical Activities & Monitoring are to be identified and implemented by Supervisory staff.
D | Unlikely | Could occur, but would not be expected - 10 - 30% probable | 4 | Major | Single fatality, permanent localised environmental harm. Substantial risk to corporate reputation, sustained adverse local media coverage, major repairs or project outcomes affected, or expected financial impact = $1 - 10 mill. | D | L (3) | M (6) | M (10) | H (15) | H (19) | LOW-The work is relatively safe and can be managed by following routine MMRs, procedures, guidelines & JSEA/SWMS. No further action is required, unless additional hazards arise during the work.
E | Rare | Rare that this would occur - no previous occurrence in similar circumstances - < 10% probable | 5 | Catastrophic | Multiple fatalities, permanent long term and extensive environmental harm. Extreme risk to corporate reputation, public outrage & national media coverage, high profile litigation, class action, threat to business division viability or expected financial outcome = $10 - $100 mill. | E | L (1) | L (2) | L (5) | M (9) | H (14) | HIERARCHY OF CONTROLS Eliminate - remove hazard completely; Substitute - replace with less hazardous; Isolate - separate the worker from the hazard Engineer - guarding, mechanical aids, ventilation; Administrate - reduce exposure, procedures, consultation; PPE - to be used in addition to above.
Mirvac HSE
Element 3 - Risk Management
Risk & Opportunity Register
Mirvac HSE
Element 3 - Risk Management
Risk & Opportunity Register

## Typical Hazards & Aspects
Typical Significant Hazards & Aspects Checklist
CONTACT WITH ELECTRICITY - Any contact with electricity by person or by plant /vehicle leading to potential electric shock to a person. | HOT WORK - Any Flame or Spark producing activity - welding, gas-cutting, grinding which may cause fire or injury. |  | EFFECTS ON COMMUNITY - Any activities that may lead to actual or perceived degradation of the local community environment e.g. heavy traffic, parking, noise or negative interaction with project personnel.
FALLING OBJECTS - Potential for objects, tools, materials to fall to levels below and cause injury or damage. | MANUAL HANDLING - Stress to muscles from repetitive movements, sudden loading, incorrect lifting, handling techniques or overloading. |  | DISTURBANCE TO FLORA & FAUNA - Disruption, damage or injury to animals, their habitat or local trees, vegetation and plants.
MOVING PLANT/ VEHICLES - Potential collision between items of moving plant/ machinery, or vehicles or contact with persons | CABLES UNDER TENSION - Pre & Post Stressing of concrete. Come-along or chain-block use, hoists and slings. |  | VIBRATION - Vibration from activities that may have a physical effect on the surrounding environment.
MOVING PARTS & STORED ENERGY - Person hit by suspended / flying object, contact with or entanglement in moving parts. | STRUCTURAL FAILURE - Falsework, Formwork & Masonry walls. Collapse or loss of the load-carrying capacity of a component or the structure itself. | SOIL EROSION & SURFACE RUN-OFF - Loss of ground material due to wind/ water action, causing potential siltation/ pollution of waterways. | ENDANGERED SPECIES - Incorrect management, habitat control & identification of endangered species in the local environment.
SUBSTANCES INCLUDING CHEMICALS, GASES & DANGEROUS GOODS - Potential contact to eyes, skin or lungs with Hazardous Substances or Dangerous Goods. | EXCAVATION/ PILING/ BORING/ TRENCHING - Fall of material causing engulfment, persons falling, plant overturning, flooding, contact with underground services. | CONTAMINATED / ACID SULFATE SOIL - Incorrect management/ identification of contaminated or ASS soils. | HERITAGE ISSUES - Incorrect management, consultation or identification of local cultural or heritage issues.
HAZARDOUS MATERIALS - Asbestos, Lead, Polychlorinated Biphenyls (PCBs), synthetic mineral fibres or other as identified causing significant illness. | WORK IN CONFINED SPACES - Areas identified as having potential atmospheric contamination, lack or excess of oxygen or engulfment by free-flowing solids or liquids. | SPILLS OR DISCHARGE CAUSING CONTAMINATION - Discharge & transfer of fuels/oils (hydrocarbons), hazardous substances, dangerous goods, concrete truck wash-out. | DEVELOPMENT APPLICATION REQUIREMENTS - Failure to properly evaluate and implement critical controls may lead to environmental harm, non-conformance, fines and damage to Mirvac reputation.
OCCUPATIONAL NOISE - Workplace noise levels from activities, plant or equipment which has the potential to cause hearing damage to persons in the vicinity. | WORK AT HEIGHT - Potential for persons to fall from an elevated position and sustain a significant injury. | AIR QUALITY - Potential for pollution by dust, from wind action, disturbance of soil by vehicle/ plant movements. Exhaust emissions from plant/vehicles.
PROJECTILE FIRING TOOLS - Hilti or Ramset explosive charge tools and air or gas powered Nail guns. | WORK OVER OR NEAR WATER - Potential for persons/ plant to slip/ fall into water and risk of drowning. | WASTE - Incorrect management of solid/ liquid waste streams leading to contamination of the environment e.g. bulk earthworks, dewatering, concrete & paint.

## Risk & Opportunity Register
RISK & OPPORTUNITY REGISTER
Risk Ranking - Insert the "Untreated Risk" from the "Hazard / Aspect Worksheet" and then, according to the "Critical Controls" listed, and using the Risk Ranking matrix (Section 1) assess the "Treated Risk Ranking" appropriate to each row.
Appropriate R & O Register Hazards/Aspects and Critical Controls to be included in all workplace activity JSEAs (or equivalent)
Element | Risk | Untreated Risk | Critical Controls | Hierarchy of Controls | Critical Activities | Monitoring Activities | Treated Risk | Responsible | Legal and Other Requirements
ACCESS & EGRESS
Fire & Emergency egress | Confusion Lack of control Trips and Falls Fatalities | H17 | • At the time of design and construction the property complied with relevant AS, BCA or construction guidance - (Ordinance 70 if prior to AS). • All Emergency access & egress points must be clear of obstructions at all times. • All emergency and exit lighting is operational. • Regular Tests and Evacuation drills are conducted. | Engineering | • Fire audit to confirm compliance. • Workplace Inspections undertaken according to Mirvac schedules. • Emergency lighting maintenance undertaken as per WRMP. • Contracts established to undertake fire drills and inspections to meet regulations. | Records of: • Fire audits and Compliance certificates. • Workplace inspections. • Evacuation drills, current evacuation diagrams and signage. • Evaluation of evacuation. | M6 | Asset Manager, Facility Management team, Service Providers | WHS Act 2011 Part 2 Health & Safety Duties WHS Regs 2011 The Building Code of Australia (BCA) The Disability Discrimination Act (DDA) AS/NZS2293.1:1998 : Emergency evacuation lighting for buildings - System design, installation and operation. AS 1851-2012 : Routine service of fire protection systems and equipment MO&I HSEP4.11- Access, Egress and Working Space Service Provider Service Level Agreement MO&I Standard System Control Measures 1.0, 17.0, 17.1 45 Property had a major upgrade from a BCA Class 5 commercial proeprty to Class 9B education facility. Navitas DA & applicable FER apply strict population controls to all their levels for student and staff number. Register available on the Group HSE Sharepoint Site.
HSE Alert # 96 Preventing unauthorised access | Fall from height, personal injury | H22 | • Ensure that responsibility for verifying site security is clearly defined. • Ensure perimeter security is appropriate based on level of risk and hazards present within site boundaries. • Ensure that all fall risks are adequately controlled i.e. fenced off and any structures/equipment that present a fall risk are non-climbable • Installation of striker plates to perimeter doors | ENG / ADMIN | • Ensure that routine inspections are implemented during operating hours and at shut down to check that site security measures are in place and effectively functioning to prevent unauthorised access. | Records of Workplace inspections. Monthly FCR36 | L5 | Asset Manager, Facility Managent team, Service Providers
Public access around hazardous activities | Public exposure to hazardous activities | M12 | • Service Provider & maintenance to erect adequate barricades/ hoardings/ signage in accordance with agreed JSEA/SWMS. • Inductions to cover Mirvac's requirements. | Isolation | • Mirvac staff aware of all activities in public areas, • JSEA/SWMS checked by facility management team to ensure they are suitable for the designated area. | • Regular workplace inspections. | M6 | Asset Manager, Facility Management team, Service Providers
Building population numbers controls. Requirement as per FER & DA conditions | Navitas tenancy floors student/staff oer population | H17 | DA & Fire Engineered Report apply strick condition to tenant Navitas occupied levels Ground, 1,2,3,4,5,6,8,9,10,11,12,13,14 & 15. | Administration | Navitas manage numbers as per FER & Da conditions without exception. Mirvac provided a monthly updated monthly level by level monthly population document to confirm populaation at any given time | Mirvac FM & security has a copy of the document should an inspection from Sydney Council or F ire & Rescue NSW occur to confirm numbers meet the conditions. Navitas security & FM their process with the same document. | M6 | Asset Manager and Facility Managent team
Safe access though public areas/common areas | Slips, trips & falls | H16 | • Floors to be designed to have complaint slip ratings, non compliant surfaces to be identified and managed accordingly. • Quick response to inclement weather or spills. | Administration | • Annual slip testing to take place • Workplace Inspections undertaken according to the WRMP and service provider cleaning agreement. | • Workplace Inspections undertaken according to the WRMP and service provider cleaning agreement. • Discuss and advise tenants to assist in ensuring floors are free from risk where possible. • Cleaning rotation inspections as per SLA. • Records of Workplace inspections. | M6 | Asset Manager, Facility Management team, Service Providers
AIR QUALITY
Indoor and outdoor air quality | Adverse reactions to chemicals, particles and/or substances in the air | H16 | • Provide clean, healthy, fresh air to facility at all times. • Ensure adequate ventilation. • Ensure recommended chemicals and treatments are used in the correct quantities at all times. • Plant, equipment and filters are inspected and cleaned on a regular basis. • All chemicals to be used in accordance with the Safety Data Sheet (SDS). | Engineering | • Annual air quality testing for bacteria, CO’s, temp and humidity, or at more frequent intervals if deemed necessary. • Corrective and preventative actions implemented and recorded for any out of parameter levels. | • Monthly testing of water system quality. • Service Provider to be regularly monitored to ensure inspections are completed as per the SLA. | M6 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 (s)40 – 41 General Working Environment. (s)49 – 52 Managing risks from airborne contaminants & Hazardous Atmospheres AS3666-1995 Air handling and water systems of buildings - Microbial control AS1668.2-1991 Mechanical ventilation for acceptable indoor air quality AS1324-1996 Air filters for use in general ventilation and air-conditioning MO&I E&O Procedure- Indoor Air Quality MO&I Standard System Control Measures 3.0, 4.0
BIOLOGICAL
Infection control | Exposure to blood borne infectious diseases | H16 | • Ensure blood/faeces are cleaned up immediately after reporting, ensuring cleaners adherence to their own company procedures. • Ensure hypodermic needles, syringes, condoms or other, are collected immediately after they are reported utilising the recommended containers and tools as per SWMS / JSEA. | Elimination | • Provide appropriate training, equipment and PPE for managing biological hazards. • Dispose of biological waste in accordance with SWMS / JSEA. | • Service Provider to be regularly monitored to ensure activities are completed as per the SLA. | L3 | Asset Manager, Facility Management team, Service Providers | WHS Regulation 2011 (s)42 First Aid AS4031 Non-reusable containers for the collection of sharp medical items used in health care areas. National Code of Practice: Control of Work Related Exposure to Hepatitis and HIV (blood-borne) Viruses [NOHSC: 2010 (2003)] Mirvac Group Sharps & Blood Borne Disease Management Procedure- MO&I Standard System Control Measures 29.0
| Exposure to infectious viruses | H19 | • Ensure Government guidelines on physical distancing can be achieved in the workplace. • Ensure that appropriate signage is displayed advising of conditions of entry and physical distancing requirements within the asset. People who are unwell will not be permitted access. • Ensure all contractors confirm compliance with control measures prior to accessing the asset. • Ensure that all high touch points are disinfected on a regular basis each day in accordance with Department of Health cleaning standards. • Ensure adequate sanitary, cleaning and PPE supplies are available. • Ensure building occupants are aware that they must report a suspected or confirmed case to building management immediately. • Ensure social distancing is maintained at seating areas (apply signage to fixed furniture, remove furniture where appropriate). • Ensure sanitisation stations are available in each lobby / EOT. | Elimination | • Provide appropriate training, equipment, PPE and resources for managing infectious viruses. • Ensure that potentially contaminated areas are disinfected immediately following a report of a suspected or confirmed case. • Ensure contact tracing is undertaken and relevant parties notified as soon as practicable. • Ensure infected individuals isolate for 14 days and obtain medical clearance before returning to the workplace | • Service Provider to be regularly monitored to ensure activities are completed as per the SLA. • Monitor reports from tenants. | L3 | Asset Manager, Facility Management team, Service Providers
COMMUNITY CONTACT
Community contact | Public safety Brand reputation Adverse media coverage | M10 | • All contact from the community including complaints, reports etc. are to be registered in iSystain within 24 hours • All media enquiries to be directly managed by the Mirvac Communications Team. | Administration | • Respond to complainant within 48 hrs. | • Records maintained in iSystain. | L3 | Asset Manager, Facility Management team, Service Providers | Environmental Planning & Assessment Act Mirvac Group form Community Contact Notification MO&I Standard System Control Measures 4.0, 22.0, 22.1, 22.2, 37.0, 50.0
CONTACT WITH ELECTRICITY
Electrical tools & equipment | Electrocution or fire | H22 | • Industrial rated tools and equipment only including leads and plugs. • Elevation of leads and protection with plastic stand hooks; • Use of portable RCDs as required. • Ensure all electrical equipment is used and maintained as per manufactures recommendations and operational manuals. | Engineering | • Pre-start check of condition of leads and tools and check within test date; • Lock out/tag out all faulty equipment. • Ensure all equipment is currently tagged and tested. | • Electrical tag and testing records | M10 | Asset Manager, Facility Management team, Service Providers | WHS Act 2011 Part 2 Health & Safety Duties WHS Regulation Chapter 4 Part 4.7 General electrical safety in workplaces and energised electrical work AS/NZS 3760:2010 : In-service safety inspection and testing of electrical equipment AS/NZS3012:2010 : Electrical installations - Construction and demolition sites Mirvac Group Electrical Inspection & Testing Guidelines Mirvac Electrical Inspection & Testing Register Mirvac Isolation Procedure MO&I Standard System Control Measures 16.0, 44.1
Electrical Installation (switch board) Supply (transformer) Working on Switchboards and TDB | Electrocution Fire Non compliant electrical work | H22 | • Adequate and compliant switch boards and wiring provided; • Residual Current Devices (RCD) installed. • Determine if any onsite transformers are owned by either the electrical authority or Mirvac. • Use of rated conduits for temporary wiring; | Elimination | • Annual testing of RCDs. • Annual Thermography Scans undertaken. • Isolation stickers are provided where required. • Implement corrective and preventative actions as required. | • Record of annual Thermoscan Report. • Regular inspection of workplace as per FCR36. | M10 | Asset Manager, Facility Management team, Service Providers
Electric welding | Electrocution Burns Fire Property damage | H22 | • Compliance of switchboards with AS3012 with 30Amp socket provided at all switchboards; • Welding earth situated close to welding location and attached to clean & conductive surface; • Voltage Reducing Device (VRD) used in wet conditions or if working on or in conducting material (Cat B & C); • Training and competency; • Electrical PPE (mats, gloves, face shield); • Emergency Management Plan in place and tested. | Engineering | • Performance of VRD tested by qualified electrician quarterly • Welding undertaken by a qualified welder. • Dry welding glass gloves used by person conducting welding. | • Record of competency provided. • Records of testing & inspection. | M10 | Asset Manager, Facility Management team, Service Providers
Overhead power lines | Electrocution Falls from height | H22 | • Reroute the work or reroute the overhead service to avoid contact with overhead services; • Use smaller plant (smaller design envelope) or insulated scaffold components; • Selection of insulated plant and equipment; • Power lines isolated when work is within prescribed distances; • Insulated barriers to prevent access within the exclusion zone; • Slewing and height restrictors; • Safe approach distance as per voltage and Work with Services MMR (distance in air from power line and any person, or object held by, or in contact with a person) applies in any direction where metallic scaffold is erected, used or dismantled near overhead power lines up to and including 33,000 volts; • Plant & equipment maintains prescribed distances according to voltage: • Up to & including 132,000 volts - 3.0 metres • Above 132,000 & including 330,000 volts - 6.0 metres • Above 330,000 volts - 8.0 metres; • Goal posts and bunting on entry points and bunting below wires; • Spotter in place for the work; • Tiger tails on wires; • Training and Competency; | Engineering | • Power lines highlighted with 'tiger tails' • Exclusion zone marked for overhead cables and signage displayed • Spotter assigned for High Risk work • Hydraulic limiters installed on plant & equipment capable of reaching into exclusion zone. • Electricity Authority permits issued for work within prescribed distances • Earthing of overhead conductors is visible (e.g., earthing clamps) | • On-site observation • Records of Regulatory Authority Permits and training On-site observation | M10 | Asset Manager, Facility Management team, Service Providers
Underground power cables | Electrocution Loss of power | H22 | • Design the work to avoid existing underground services; • Utilise safer digging method (non-destructive digging), ceramic handled shovels for pot holing; • Use of GPR and cable locators to accurately identify existing services; • Etraction of hard barriers to protect from contact with the service; • Use of pot holing to positively identify service routes; • DBYD and As Constructed drawings to identify location and age of service; • Hold points in the work as per Excavation Piling Boring Trenching Permit; • Dedicated safety spotter during the works. | Engineering | • Survey of excavation areas including 'As Executed' drawings and Dial Before You Dig (DBYD) • 'Potholing' to visually confirm location/depth and mark routes/depth on survey pegs. • Issue Mirvac Excavation Permit including up to date drawings | • Records of Survey/Drawings, DBYD, and Drawing Register • On-site observation | M10 | Asset Manager, Facility Management team, Service Providers
Drilling/Saw cutting into slab with energised in-situ electrical cables | Electrocution Loss of power | H21 | • No drilling or cutting into slab (> 40mm) with live electrical cables unless approval has been given by Mirvac centre management. • Slab scans to be completed is approval is given • Check at switchboard locations or underside of floors to determine if conduits and / or cables enter / exit the structure / slab etc. • Barricading is to be erected around areas to be cut to ensure only those involved have access. The slab must be cut into block sizes that can be lifted by a crane or a lifting device approved by a competent engineer. • For any work involving cutting, nailing, coring or drilling where work is within 3m of a known electrical, gas, water or telecommunications service the Coring Chasing Concrete Cutting Permit must be completed. A Permit must also be completed where the depth of the penetration is >40 mm or is determined by risk assessment to require one. | Engineering | • In the event of drilling or cutting into a slab that has live electrical cables, once assessed by site electrician and Mirvac Workplace Manager if the area has potential for live cables in that area then a Mirvac Coring permit must be complete, where isolating all power to that area will be ensured. • Toolbox talk and consult service providers on procedure and when slabs are energised, communicate at subcontractors meeting. • All services must be marked-up using a non-water-soluble fluoro marker plus on the site plan before work starts. High voltage cables must also be sign posted with their location. | • Records of Consultation • Coring/Chasing permit • Scan record • On site observations | H15 | Asset Manager, Facility Management team, Service Providers
Undertaking Electrical Work on or near energised services (installation, commissioning, maintaining, fault finding, isolating, testing, re-energising) | Electrocution Explosion | H22 | • Person not working on 'live' equipment (e.g., Distribution Board or circuit isolated & locked out); • Hard barriers to maintain safe approach distances and prevent inadvertent contact; • Rated insulation/intrinsically safe tools to protect if contact occurs; • Isolation Lockout Tagout MMR and personal locks; • Earth leakage protectors and inbuilt fault tripping; • Isolation Lockout Tagout Permit; • Training and Competency; • Emergency Recue Kits and Standby Person; • Electrically rated PPE, mats, gloves, multimeter; • Electrical Handover processes and certificate. | Engineering | • Person is licenced electrician using Service • Provider Isolation Procedure or trained in Mirvac Isolation Procedure | • Record of competency & isolation training provided • Physical lock out/isolation system observed in operation • Register of lock out/isolation system implementation | H19 | Asset Manager, Facility Management team, Service Providers
CONFINED SPACES
Entry into confined space • Grease traps - Basement 1 • Pits (Lifts) G, B1 & B6 • Storage & Retention Tanks - Level 16 & B6 • Cooling towers - 1, 2 & 3 level 16 • Drainage pits - Basement 6 | Entry by unauthorised person | H20 | • Design out and eliminate the need to enter confined spaces where possible; • Confined spaces labelled and access restricted (e.g. Key locked, signage, barricade) (isolation); • Maintain a register and risk assessment for Confined Spaces (administrative) • Confined space entry controlled through permitting system (administrative);Design out confined spaces where possible; | Isolation | • Confined space entry permit completed by person trained in confined spaces (by RTO with confined spaces in their scope). • Entry restricted to persons with confined space training certificate. • Person that accepts risk assessment is trained in risk assessment • Standby person at confined space entry point controls entry and exit • Gas monitor has a current calibration and is 'bump tested' in fresh air prior to each use. • Emergency retrieval system has been prepared or authorised by a person that is confined space trained (by RTO with confined spaces in their scope). | • Register of Identified Confined Spaces and risk assessment. • Record of training • Register of persons entry/exit to space | H15 | Asset Manager, Facility Management team, Service Providers | WHS Regulation 2011 (s)291 (f) Meaning of ‘high risk construction work” WHS Regulation 2011 sections 62 - 77, Confined Spaces, WHS Regulations 2011 (s)81 - 112, High Risk Work National Code of Practice : Confined Spaces AS/NZS 2865:2009 Safe Working in a Confined Space - s12 Mirvac Group Confined Space Entry Procedure HSEP4.09 Mirvac Group Confined Spaces Entry Permit MO&I Standard System Control Measures 3.0, 9.0, 20.0, 25.0, 39, 40.2, 54.10
CONSTRUCTION ACTIVITIES
Principal Contractor construction activities | Injuries to people, damage to property and the environment | H16 | All construction works over $250,000 ($350,000 VIC) performed on site must have an appointed Principal contractor. All construction works below this amount must have a licensed builder. Principals Contractors must be appointed in accordance with the Mirvac Principal Contractor Management Procedure. Mirvac Contractor Registration & Qualification Process to be undertaken by Principal Contractor in consultation with HSE. Contractors to follow and abide by their own SWMS/JSEA for specific work being undertaken. | Administration | A representative from the PC is to undertake the Mirvac Contractor Registration and Induction process. All employees and subcontractors of the PC must undertake the PC's induction for the project. If a PC is not required to be appointed, all contractors must follow the Mirvac Contractors Registration and Induction process. A representative from the PC is to log in/ out of contractor management system (CMS) daily whilst works are being undertaken. PC employees and subcontractors conducting building impact works must sign in/out of the CMS terminal. | BM to conduct periodical inspections of construction as per FCR37. Implementation Review to be undertaken by HSE. | M10 | Asset Manager, Facility Management team, Service Providers, HSE | WHS Regulation 2011 Chapter 6 Construction Work Mirvac Standard Terms & Conditions Mirvac Registration & Qualification overview letter Mirvac Step by Step Guide to Registration & Qualification MO&I Standard System Control Measures 1.0, 10.0, 38.0
Construction activities Refurbishments/Refit etc. | Injuries to people, damage to property and the environment | H16 | All construction works under $250,000 ($350,000 VIC) must be completed by a licensed contractor. Mirvac Contractor Registration & Qualification Process to be undertaken by Mirvac contractors and tenant contractors undertaking building impact works. Contractors to follow and abide by their own SWMS/JSEA for specific work being undertaken. | Administration | Contractors to log in/ out of contractor management system (CMS) daily whilst works are being undertaken. BM to review CMS for site access and compliance. | All contractors and tenant contractors conducting building impact works must complete Mirvac registration and induction process prior to starting works. BM to conduct periodical inspections of construction as per FCR37 | M10 | Asset Manager, Facility Management team, Service Providers
CONTRACTOR MANAGEMENT
Mirvac and Tenant Contractors | Injuries to people, damage to property and the environment | H17 | • Mirvac Contractor Registration & Qualification Process to be undertaken by contractor. • Contractor audit FCR37 to be conducted twice a month. • Review SWMS to ensure adequate control are identified in SWMS. • Contractor to follow Mirvac HSE Management System | Administration | • Contractors to log in/ out of contractor management system (CMS) daily whilst works are being undertaken. • FM to review CMS for site access and compliance | • Completion of Mirvac General and Workplace Specific inductions prior to attending site. • FCR 37 • HSE Observations | M10 | Asset Manager, Facility Management team, Service Providers | WHS Regulation 2011 – Chapter 6 Construction Work Mirvac Standard Terms & Conditions Mirvac Registration & Qualification overview letter Mirvac Step by Step Guide to Registration & Qualification MO&I Standard System Control Measures 10.0 HSEP4.50 Contractor Procedure
COOLING TOWERS
Cooling Towers - 1, 2 & 3 level 16 | Legionnaires disease Respiratory failure | H21 | • Management of cooling towers to be in line with the Mirvac Retail Cooling Towers Manual to ensure adequate water treatment and cooling tower monitoring process is maintained. • Bacterial water testing to be inducted on a monthly basis. | Administration | • Implementation of the Mirvac Retail Cooling Tower Manual. • Engagement of suitable qualified service provide for water testing and cooling maintenance. | • Inspections as per cooling tower manuals. • Monthly testing of cooling tower water, follow-up of corrective action for any out of parameter readings. | M10 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 (s)40 – 41 General Working Environment. (s)49 – 52 Managing risks from airborne contaminants & Hazardous Atmospheres AS3666-1995 Air handling and water systems of buildings - Microbial control AS1668.2-1991 Mechanical ventilation for acceptable indoor air quality AS1324-1996 Air filters for use in general ventilation and air-conditioning MO&I E&O Procedure- Indoor Air Quality MO&I Standard System Control Measures 4.1, 4.2
EMERGENCY PREPAREDNESS
First Aid | Injuries to people, damage to property and the environment, including escalation | M11 | • First aid officer to undertake competency-based training form a RTO. • A first aid officer to be on shift at all times. • First Aid Officer poster to be displayed in all visible locations. | Administration | • Site Specific Procedures Manual to be held on site. • BM to ensure evacuation plans (with identified “you are here” stickers) are in place and displayed at Mirvac Retail workplaces. | • Observe that evacuation plans are in place and displayed in prominent locations. • Regular evacuation training is provided to tenant employees including first aid (supplies and training). | L2 | Asset Manager, Facility Management team, Service Providers | WHS Act 2011 (s)20 Further duties of PCBU WHS Regulation 2011 (s) 42-43 First Aid & Emergency Plans WHS Regulation 2011 (s) 39 & 43 General Workplace Management AS3745 Planning for Emergencies in Facilities AS1851 Routine service of fire protection systems and equipment AS1319 Safety signs for the occupational environment Mirvac Group Emergency Response Procedure Mirvac Group Lock Out/Tag Out Isolation Procedure Site Specific Procedures Manual MO&I Standard System Control Measures 1.0, 17.0, 17.1, 20.0, 21.0 HSEP4.55 First Aid Procedure
Naturals disasters | Loss of life, property and interruption to business operations | H22 | • Senior management to be involved to review the location (proximity to hazard – flood prone areas/bush fire zones) and type of asset (structure - to determine if the risks to the asset can be eliminated or minimised. • Flood prevention and mitigation strategies to be developed in line with local government recommendations. All new builds and refurbishments are to undergo the DOOR process to ensure Flood/Bushfire risk may be reduced by the design. | Administration | • Where the risk is present as determine by the DA or council requirements, the development of a flood/bushfire management plan linked to the Emergency Response/business continuity plan (BCP) is to completed and implemented (communicated) into the facility overall site specific procedures. | • Weather events which have the likelihood to impact the property are to be monitored through local and state media (bureau of Meteorology, News (TV/Radio) stations. | L3 | Asset Manager, Facility Management team, Service Providers
Evacuation/Bomb Threats | Damage to Property | H22 | • Evacuation and control procedures documented by Mirvac Retail specific emergency evacuation consultant. Documents to be held on site by site team. • Procedures to be practiced regularly. • Document to be reviewed on a regular basis. | Administration | • Where the risk is present as determine by the DA or council requirements, the development of a flood/bushfire management plan linked to the Emergency Response/business continuity plan (BCP) is to completed and implemented (communicated) into the facility overall site specific procedures. | • Weather events which have the likelihood to impact the property are to be monitored through local and state media (bureau of Meteorology, News (TV/Radio) stations. | M9 | Asset Manager, Facility Management team, Service Providers
Fire | Fire, loss of life and property | H15 | • All buildings to include fire protection systems to detect and prevent the spread of fire. • Fire systems to be identified in Emergency & Evacuation Management Plans • All isolations of fire systems to be recorded by “Isolation Permit” at Building Management as well as isolation log book at FIP. | Administration | • Verification of annual Maintenance requirement – Service Providers to comply with AS1851 (Routine service of fire protection systems and equipment) • Emergency Evacuation training for all employees and use of certain fire equipment (QLD/ fire extinguisher). • All systems and equipment to be tested as per AS 1851 and certified by contractor allow the Annual Fire Safety • Statement to be completed and issued to council, as well as Insurers and National Ops Mgr. advised of impairments and of their return to service. | • Fire system inspection and critical dates maintained as per Mex requirements. • Annual Emergency Evacuation Drills. • Bi- Annual Emergency Control Organisation (ECO) training. | L5 | Asset Manager, Facility Management team, Service Providers
ESCALATORS AND LIFTS
Escalators and lifts | Entrapment, falls from heights, crush injuries | H20 | • Lifts & escalators operation and maintenance must be in compliance to Mirvac Retail Lifts & Escalators Procedure. • Regular inspections to be undertaken. | Isolation | • Lifts & Escalators are to be covered by comprehensive (maintenance) contracts provided by recognised lift maintenance companies. | • FM to carry out routine inspections of lifts and Escalators or as per FCR36 requirements. | M9 | Asset Manager, Facility Management team, Service Providers | WHS ACT 2011 – (s)21 - Duties of PCBU involving management or control of fixtures, fittings or plant at workplaces AS/NZS 1735 Lifts, escalators and moving walkways MO&I Lifts, Escalators and travelators procedure MO&I Standard System Control Measures
EXCAVATION/PILING/BORING/TRENCHING
Standard Excavation | Injuries to people, damage to property and the environment | H15 | • Hazardous/contaminated soils (hot spots) identified; • No contact with underground services (e.g., power cables, gas, communications or other services). • Identification of soft ground/ soil which may be subject to collapse once excavated. • People that are not part of work crew are not in excavation; • Trench is effectively shored, benched or graded at no more than 45 degrees when deeper than 1.5 metres; • Equipment, plant, materials or spoil is not within • 1 metre of edge, or within the "zone of influence". • Any trenches, pier holes, pits, and other penetrations deeper than 1.5 metre are not left opened and unattended, and are backfilled, covered or barricaded and signposted "Penetration Below". • Excavator boom and bucket not slewed over workers. • People clear of area in trench when lifting is being undertaken. • No person to work alone in trench unless spotter is present. | Engineering | • Soil test to be carried out by NATA certified lab (for tests being used) • Survey of excavation areas including 'As Executed' drawings and Dial Before You Dig (DBYD) • 'Potholing' to visually confirm location/depth of services and mark routes/depth on survey pegs. • Use of Excavation Permit including up to date drawings • Access to excavation area is controlled by use of barricades and signage (and spotter if required). • Excavations are accessed at 9 metre intervals along trench. • Ladders/scaffold stairs fixed at top and bottom and to extend 1m above ground level. • Daily inspection of trench walls completed by competent person • Daily inspection of trench walls and surrounding area completed by competent person • Machine operator is licenced • Spotter in sight of operator at all times • Trenches, pits or other penetrations secured at the each of each day or when unattended | • Soil test records • Management plan in place • Records of surveys, drawing registers and DBYD/As Executed drawings available • DBYD/As Executed Drawings attached to permit • Records of Excavation Permits • As Executed Drawings, drawing registers updated with new services installed • On-site observation • Records of inspection | M9 | Asset Manager, Facility Management team, Service Providers
Deep Excavations e.g., greater than 3 metres | Injuries to people, damage to property and the environment | H20 | • Controls above • Documented emergency retrieval system exists and is able to be enacted if required (trialled via drills) | Engineering | • Activities above • Emergency retrieval system has been prepared or authorised by a person that is confined space trained | • Activities above • Record of training • Records of evacuations and training drills | H15 | Asset Manager, Facility Management team, Service Providers
FALLING OBJECTS
Stationary Working Platforms (e.g., scaffolds, elevated walkways, trestles) including collapse | Object falling from height Hit / Strike employee or member of public | H16 | • Use of physical barriers to prevent objects dropping (containment meshing); • Brick guards fitted where potential for falling objects exists; • Protection of the structure from being hit by loads or mobile plant; • Toe boards installed; • Scaffolds, walkways, elevated work areas e.g., slabs, roofs have toe boards installed.; • Work within the design rating of the equipment; • Management of Change process to ensure integrity is maintained when structure changes; • Scaffolding design drawings and plans and checks that construction is compliant. | Isolation | • Handover certificate received • Mirvac inspection prior to acceptance. | • Records of Certificates and Inspections • On-site observation | M10 | Asset Manager, Facility Management team, Service Providers
Mobile Working Platforms (e.g. Elevated Work Platform (EWP), Scissor Lift, Swinging Stages, mobile scaffolds) | Object falling from height Hit / Strike employee or member of public | H16 | • Staging of the work when no one else around; • Separated work fronts to avoid simultaneous operations; • Adhere to minimum standards for design compliance; • Exclusion zone implemented • Work within the design rating of the equipment; • Management of Change process to ensure integrity is maintained when structure changes; • OEM requirements complied with; • Processes for the management of Design of Temporary Works; • Plant Arrival Checklist; • Plant Risk Assessment; • Plant maintenance and inspection regime; • Verification of Competency for operators; • High Risk Work Licenses where required (e.g. scissor lift over 11m). | Elimination | • Handover certificate received • Mirvac inspection prior to acceptance • Exclusion zone marked and maintained | • Records of Certificates and Inspections • On-site observation | M10 | Asset Manager, Facility Management team, Service Providers
HAZARDOUS SUBSTANCES
Storage and Handling of Hazardous Substances | Spills or discharge causing contamination Injury/Illness of Member of Public, Contractor or Worker | M10 | • Substances/goods stored and handled in accordance with SDS (Safety Data Sheet). • Appropriate bunding for hazardous chemicals with a minimum of 110% capacity. • Untrained people not to use or determine storage requirements for hazardous substances or dangerous goods • Products stored in approved cabinets or purpose-built containment areas • Hazardous Substance Risk Assessment completed including research and purchase of less hazardous/ dangerous products • All users of hazardous substances appropriately trained and have adequate PPE • Spills kits in stock • Appropriate First Aid facilities including eye wash stations | Substitute | • Products & Hazardous Substances Register completed listed • SDS (Safety Data Sheet) for all products in use, issue date less than 5 years old. • Hazardous Substance Risk Assessment completed for all products/substances/goods classified as hazardous • Products/substances labelled • Person trained in storage and use of hazardous substance and dangerous goods as outlined on the HSRA and in the MSDS (SDS) • Appropriate number of spill kit and in appropriate locations | • Records of MSDS (SDS) • Spill Kit stocked and audited. • Records of spill response training available. • On-site observation. • Drainage outlet to bunding locked. | L5 | Asset Manager, Facility Management team, Service Providers | WHS Regulation 2011 subdivision 4 Storage and Handling Systems National Code of Practice - Managing Risks of Hazardous Chemicals AS 1940:2004 Storage and Handling of Flammable and Combustible Liquids - cl 5.8; AS 4452:1997 Storage and Handling of Toxic Substances - cl 5.7; Mirvac Group Hazardous Substance Dangerous Goods Management Procedure MO&I Chemical, Hazardous Substances, Handling and Storage Procedure HSE1.07P MO&I Hazardous Substances Register MO&I Standard System Control Measures 7.0, 12.0, 12.1, 12.2, 12.3, 12.4, 14.0, 54.6
HAZARDOUS MATERIALS
Asbestos, Lead, Polychlorinated Biphenyls (PCBs), synthetic mineral fibres, lead or other as identified (also refer Asbestos in Occupational Exposures Section) | Asthma, skin rashes, allergic reactions, allergic sensitisation, cancer, and other long term diseases from exposure to substances. | H22 | • Hazardous material survey to be conducted on all assets built before 2003 and if materials found a new survey to be completed every 5 years. • All identified asbestos must be labelled with the type and nature of the material (friable/non-friable). • Removal of asbestos to be conducted by licensed removalist. • Hazardous material to be disposed of in accordance with Local, State and Federal Legislation. • If suspected asbestos is found in asset it is to be treated as Asbestos; • Asbestos is to be wet down, National HSE Manager be notified, tests to be completed to determine if it is Asbestos. | Administration | • Hazardous Material Survey to be reviewed prior to any work commencing • Contractor licensed by Environmental Regulatory Authority (ERA) • Transporter and receiver of waste are ERA Licensed • Waste transport certificate is obtained. • Signage and emergency response equipment available relevant to the class of substance/good stored. | • Records of survey/ licenses • Hazardous Materials - 5 yearly inspection of areas containing Asbestos by a competent person. • A Register of all Hazardous Materials to be kept on site. | H14 | Asset Manager, Facility Management team, Service Providers | WHS Regulation 2011 subdivision 4 Storage and Handling Systems National Code of Practice - Managing Risks of Hazardous Chemicals AS 1940:2004 Storage and Handling of Flammable and Combustible Liquids - cl 5.8; AS 4452:1997 Storage and Handling of Toxic Substances - cl 5.7; Mirvac Group Hazardous Substance Dangerous Goods Management Procedure MO&I Chemical, Hazardous Substances, Handling and Storage Procedure HSE1.07P MO&I Hazardous Substances Register MO&I Standard System Control Measures 7.0, 12.0, 12.1, 12.2, 12.3, 12.4, 14.0, 54.6
HEAVY VEHICLES
Vehicles with twin axel or greater | Fatigue, motor vehicle accident, unsecured load. | H22 | • Ensure that any items packed or loaded by Mirvac personnel are packed and secured safely. . | Administration | • Do not direct or encourage the driver to work unsafely (e.g. speeding or driving while fatigued). | • Monitor vehicle and driver activity on site and address any concerns immediately. | H14 | Asset Manager, Facility Management team, Service Providers
HOT WORKS
Hot work (welding, burning or angle grinding) - | Fire Burns Property damage Environmental damage | H16 | • If possible, redesign the work methodology to a non-heat producing methodology; • Non-flammable screens to protect flammable substances from the work; • If welding/cutting, gas cylinders secured and have flashback arrestors fitted at torch and gas bottle on both hoses; • Hot Work Permit used and copy at location of work; • Trained and competent operator; • Fire equipment working properly and located within 2 metres of hot work; • Spotter in place with firefighting equipment; • Fire Equipment Register and maintenance program | Engineering | • A competent and experienced person has conducted a Risk Assessment of the proposed work and inspected the workplace. • Hot Work Permit issued in accordance with the Hot Work Procedure and discussed with the person undertaking the hot work. • Include potential of falling objects and hot material from overhead Hot Works in JSEA • Review of Hot Work Permit if work conditions or location changes. • Inspection during hot work task. • Permit closed out at conclusion of hot work • 12 monthly testing/ replacement of flashback arrestors Flashback arrestors fitted by competent person (e.g. plumber, welder) • Inspection of fire equipment carried out within last 6 months • Personnel trained in use of fire extinguishers | • On-site observation • Hot Work Permit at work location, all conditions comply • Maintenance records | M10 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 Part 4.3 Confined Spaces AS 1674.1:1997 Safety in Welding & Allied Processes (Fire Precautions) - cl 3.5, Appendix A (A2); MO&I SOP1.46- Welding , Burning & Heating Building Mirvac Hot Works Permit Mirvac Registration & Qualification overview letter Mirvac Step by Step Guide to Registration & Qualification MO&I Standard System Control Measures 16.0, 25.0, 38.0 HSEP4.61 Welding, Burning and Heating Operation Procedure
LIGHTING
Lighting | Inadequate lighting causing Injuries to people, damage to property | M11 | • All designs to comply with Australian Standard Building Fit Out specifications. • Compliance with the relevant Australian Standard for LUX Levels • Task specific lighting in place as per SWMS / JSEA. | Engineering | • DOOR 4 inspection to verify sufficient lighting • Regular inspection of workplace. | • Regular lighting inspections undertaken with defects identified and reported. • Night audits completed | L2 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 AS 1680.1 Interior & Workplace Lighting AS 2293.1-2005 Emergency escape lighting and exit signs for buildings - System design, installation and operation MO&I Lighting procedure HSE 1.32P MO&I Standard System Control Measures 31.0 HSEP4.57 Lighting Procedure
MANUAL HANDLING
Activities that may include lifting, lowering, pushing, pulling | Sprains, strains and damage to joints ligaments and muscles | H16 | • Consider safe access and use in the design phase (DOOR). • Assess the risk prior to any manual handling task. Plan the task and ensure pathways are clear. Use mechanical aid or trolley where possible. • Bulk loads must be secured on trolleys to prevent toppling. • Follow SWMS / JSEA for all hazardous manual tasks. | Elimination | • Training in correct manual handling techniques (incl. on-going toolbox talks, coaching) • Maintain mechanical aids. • Monitor hazardous manual tasks to ensure compliance. | • Records of training • On-site observation • Maintenance records | M10 | Asset Manager, Facility Management team, Service Providers | WHS Regulation 2011 Sections 60 & 61 Hazardous Manual Tasks National Code of Practice for Hazardous Manual tasks Mirvac Group Manual Handling Procedure Mirvac Group Manual Handling Guideline Mirvac Group Manual Handling Task Specific Risk Assessment MO&I Occupational Overuse Syndrome Procedure MO&I Standard System Control Measures 34.0
OCCUPATIONAL EXPOSURES
Thermal Stress/ UV radiation | Illness to workers from long terms exposure | H16 | • Job rotation, provision of PPE, rest breaks, provision of thermally regulated break rooms • Limit physical work to early mornings when temperatures are cooler; • Provide adequate shade and access to drinking water; • Stop work in extreme temperatures; • PPE and sunscreen in use as per SWMS / JSEA; • All persons handling or storing hazardous chemicals/substances must undertake Occupational Exposures Training | Elimination | • Supervision of work design and task rotation; • Workplace inspection; • Monitor BOM forecasts; • Temperature and Humidity monitoring | • On-site observation by Mirvac and regular inspections | M9 | Asset Manager, Facility Management team, Service Providers
Inhalable dust/ Respirable Dust/ Crystalline Silica | Illness to workers from long terms exposure | H21 | • Use of dust minimising work practices (e.g. wet cutting) • Use of dust minimising hand tools (grinders/ saws fitted with vacuum extraction) • Use of Respiratory Protection as per SWMS / JSEA; • Project personnel alerted to substances and risk of exposure; • All persons handling or storing hazardous chemicals/substances must undertake Occupational Exposures Training | Engineering | • Workplace inspection to ensure dust suppression is adequate; • Dust monitors to be used where required | • Air quality monitoring by hygienist where required. | M10 | Asset Manager, Facility Management team, Service Providers
Diesel particulate | Illness to workers from long terms exposure | H16 | • Forced ventilation; • Use of catalytic converter when indoors; • Personnel alerted to substances and risk of exposure; • All persons handling or storing hazardous chemicals/substances must undertake Occupational Exposures Training; • Substitute with Gas power where possible. | Engineering | • Ensure design provides adequate ventilation (DOOR Process); • Plant and equipment is maintained and serviced as per manufacturers recommendations. | • Site Inspections and Audits; • Induction Records | M10 | Asset Manager, Facility Management team, Service Providers
Organophosphate | Illness to workers from long terms exposure | H16 | • Use of lowest risk chemicals/ organophosphate free where possible; • Use of PPE; • Project personnel alerted to substances and risk of exposure; • All persons handling or storing hazardous chemicals/substances must undertake Occupational Exposures Training | Substitution | • Required training occurs; • JSEA/SWMS approval process considers required controls. | • Site Inspections and Audits; • Induction Records | M10 | Asset Manager, Facility Management team, Service Providers
VOC's | Illness to workers from long terms exposure | H16 | • Hazardous substance pre-purchase risk assessment- low VOC process; • Use of forced/ natural ventilation; • Respiratory protection; • Project personnel alerted to substances and risk of exposure; • HSE Manager trained in Mirvac Occupational Exposures Training • Occupational Exposures covered in Induction Training for all workers | Substitution | • JSEA/SWMS approval process considers required controls • Required training occurs; | • Site Inspections and Audits; • Induction Records | M10 | Asset Manager, Facility Management team, Service Providers
Heavy Metals/ Weld Fume | Illness to workers from long terms exposure | H16 | • Forced ventilation • Substitute welding with lower risk work practices • Respiratory protection • Hot works permit • Project personnel alerted to substances and risk of exposure; • HSE Manager trained in Mirvac Occupational Exposures Training • Occupational Exposures covered in Induction Training for all workers | Engineering | • JSEA/SWMS approval process considers required controls; • Required training occurs; | • Site Inspections and Audits; • Induction Records | M10 | Asset Manager, Facility Management team, Service Providers
OCCUPATIONAL NOISE
Noise | Hearing loss or damage. Discomfort to the community | M11 | • Noisy activities isolated from general work areas by noise barriers wherever possible • Personal hearing protection must be work as required in the SWMS / JSEA's • Use of noise minimising tools / equipment where possible. • Appropriate respite periods to be incorporated into the job schedule. | Engineering | • Audiometric testing for at risk employees if required to wear hearing protection on a frequent basis. • Noise monitor to be calibrated according to manufacturer’s instructions, and Occupational Noise MMR. • Inspection of isolation barriers • Noise monitoring conducted where changes occur to a property. Relevant information is to be capture during design. | • Records of Noise Monitoring; • Records of Calibration; • Records of hearing test programs • On-site observations | L2 | Asset Manager, Facility Management team, Service Providers | W HS Regulations 2011 (s)56 - 59, Noise WHS Code of Practice - Managing Noise & Preventing Hearing Loss at Work AS 2436:2010 – Guide to Noise and Vibration Control on Construction, Demolition and Maintenance Sites; AS 1269:2005 Occupational noise management; AS 1270:2002 Acoustics-Hearing Protectors. Mirvac Group Noise Management Procedure HSEP4.05; MO&I Standard System Control Measures 37.0, 38.0
PLANT & EQUIPMENT
Operation of Plant and Equipment in common areas | Injuries to people Damage to property | H20 | • Exclusion zone set for all plant operating in common areas • High vis vets, reversing beepers to be used • Spotter required when plant is moving • If more than 1 plant operating in the area, a spotter is required to manage pedestrians. • Operators is licenced and competent. • Plant arrival checklist to be completed including obtaining appropriate licenses • Appropriate permit completed • Rules of operation are established (e.g., speed limits, looking in direction of travel, stopping at blind corners) | Administration | • Requirement for spotter, PPE and reversing beeper included in JSEA • Spotter rotated regularly • Operator is licenced and competent | • On-site observation • Regular inspections • Completion of FCR 36 and 37 • Record of competency • Permit • Plant Arrival Checklist | H15 | Asset Manager, Facility Management team, Service Providers | WHS ACT 2011 (s)21 Further duties of PCBU WHS Regulations 2011 Chapter 5 Plant and structures Mirvac Group Procedures Plant Arrival Checklist Plant Daily Operation Checklist Plant & Equipment Register Personal Plant & Equipment Register Mobile Crane permit MO&I HSE Procedures Electrical Safety / Hand Held Equipment and Tools / Ladders / Machinery Guarding / Office Copy Machines/ Personal Protective Clothing and Equipment MO&I Standard System Control Measures - Air Quality; Standard System Control Measures - Motor Vehicle & Driver Safety; Standard System Control Measures - Plant & Equipment 16.0, 23.0
Plant and equipment with moving / rotating parts | Injuries to people Damage to property | H20 | • Design to eliminate the risk or reduce to as low a practicable; • Appropriate machine guarding or exclusions zones must be in place; • Where possible use Interlocks to cut power to moving parts; • Plant arrival/induction checklist to be completed on all plant; • Appropriate Permit issued prior to use; • Operators trained and competent in correct use; • All plant and equipment undergo routine maintenance to OEM requirements; • All signage and warning signs in place: decals, crushing hazards, pinch points etc.; • Plant Risk Assessment; • PPE.as per SWMS/JSEA | Engineering | • Inspection of guards including adequacy of screening and fixings • Pre-operation checks and regular inspections. • Operator is competent to use equipment. | • On-site observation • Lockout Tag our Procedure. • Maintenance Schedule and Reports. • Pre-operational check and inspections. | L5 | Asset Manager, Facility Management team, Service Providers
Maintenance of plant and equipment | Injuries to people Damage to property | H16 | • Plant to be de-energised and locked out prior to commencing work. • Maintenance plan as per OEM requirements; • Maintain Plant and Equipment Register and records; • Qualified mechanics performing servicing; • Plant Risk Assessment. | Administration | • 'Test for Dead' before work commences | • Records of isolation - lock out/tag out register | M11 | Asset Manager, Facility Management team, Service Providers
PLANT ROOMS
Main Plant Room - Level 16 Sprinkler Valve Room - Basement 1 Switch Rooms - Basement 2 Lift Motor Rooms - Levels 17, 10 & B6 Fire Control Room - Basement 1 | Injuries to people, damage to property | H16 | • All plant and switch rooms are to be locked, secure with access keys to be restricted. • Unauthorised access into the plant rooms to be prevented. • Plant rooms to be free from unnecessary items and must contain sufficient lighting. | Elimination | • Access control system to be put in place to monitor access. • Appropriate signage to be installed at entries. | • Regular security checks to be undertaken to ensure enclosures remain locked and secure. • Completion of FCR36 and appropriate tenant inspections where required. | L2 | Asset Manager, Facility Management team, Service Providers | WHS ACT 2011 (s)21 Further duties of PCBU WHS Regulations 2011 Chapter 5 Plant and structures MO&I HSE Procedures MO&I Standard System Control Measures 31.0, 38.0
SECURITY
Security Operations | Armed Hold up Injuries to people, damage to property | H20 | • Facility type / tenant profile to be assessed for heightened threats. Additional controls to be included here as required. | Administration | • Discussions with Security contractor for appropriate controls as per level of threat. • Security Operations: Site Specific security procedures for various activities to be in place e.g. patrols, after hours procedure, JSEA for common activities- golf carts. | • Maintaining security procedures and business continuity plans. • Security Operations: Completion of FCR37 at regular intervals. | M9 | Asset Manager, Facility Management team, Service Providers | WHS ACT 2011 (s)20 Duties of PCBUs WHS Regulations 2011 Chapter 3 – General Risks & Workplace Management MO&I HSE Procedures– Armed Hold Up / Robbery/ Death - Suicide / Duty of Care / Emergency Procedures and Preparedness MO&I Standard System Control Measures 6.0
STORM WATER DISCHARGE
Storm Water Discharge | Environmental Damage | H15 | • Ensure that areas draining to the stormwater system are maintained and free from litter and debris. • Ensure that waste containers are provided in appropriate areas to prevent litter entering the stormwater system (for example ash trays and litter bins). • Ensure that all chemicals stored near stormwater drains are bunded to prevent leaks and spills from entering the stormwater system. | Engineering | • Provide a spill kit where appropriate, for example in car park, to ensure that oils, fuels and chemicals do not enter the stormwater system. • If appropriate, install trash racks, drain screens or separators to prevent stormwater becoming contaminated. | • FCR01 • FCR036 • Daily Operational Inspection | M9 | Asset Manager, Facility Management team, Service Providers
TEMPORARY FENCING
ATF Fencing | Injuries to people, damage to property | H16 | • Any temporary fencing must comply with AS 4687-2007 – Temporary fencing and hoardings and be erected as per manufacturers/hirers recommendations to ensure fencing can withstand impact from people and any other forces such as wind. • If shade cloth is applied, the material must allow sufficient wind permeability. | Administration | • Regular inspection and maintenance | • Asset Property Holding Inspection • FCR 01 • FCR 036 |  | Asset Manager, Facility Management team, Service Providers
TRAFFIC MANAGEMENT
Car parks Loading docks Pedestrian Management | Vehicular collision, people struck by moving objects, crush injuries and damage to property | H17 | • Implement Traffic Management Plan (TMP). • Pedestrians separated from moving plant/vehicles. • Loading Docks to be designed and operated to effectively separate pedestrian and vehicles. • Rules of operation established (e.g. speed limits, looking in direction of traffic, stopping at blind corners). | Isolation | • Where pedestrians and plant/vehicle can be separated- On-site observation/ Record of TMP and certificate of competency. • Where pedestrians and plant/vehicle cannot be separated - On-site observation/ Record of competency. • Issues and safety concerns to be raised and discussed at the tenant / retailer meetings | • Regular inspections undertaken using the MEX system of reporting and defect identification. • Appropriate signage / line marking/ barricades to be in place. | L5 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 (s)291 (n) & (o) Meaning of high risk construction work WHS Regulation 2011 (s)81 - 112, High Risk Work AS/NZS 4602.1:2011 High Visibility Safety Garments MO&I Loading Dock JSEA Facility Traffic Management Plan MO&I Standard System Control Measures 11.0, 38.0, 50.0 HSEP4.58 Traffic Management Procedure
WORK AT HEIGHT traffic Management MMR
Mobile scaffolds | Falls from a height | H20 | • Mobile scaffold installed as required including sturdy structure, fully planked, internal access with trapdoor, handrail min 900 mm, mid-rail and toe boards. • Mobile scaffolds are away from edges and penetrations • Personnel removed, tools and equipment secured prior to moving • Brakes/castor wheel locks applied whilst scaffold is in use | Engineering | • If over 4 metres, erected by licenced person • Handover certificate provided (for scaffolds over 4 metres) • Inspection of scaffold every 30 days by licenced (if > 4 m) or competent person or after adverse weather conditions • Minimum 1 metre back for every 1 metre in height of the scaffold platform | • Records of Licence (if over 4 metres) • Records of certificates • On-site observation | H15 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 (s)291 High Risk Construction Work WHS Regulations 2011 (s)54 & 55 Falling Objects AS/NZS 1892.1:1996 – Portable ladders National Code of Practice For the Prevention of Falls in General Construction Mirvac Group Working at Heights Procedure Mirvac Group Roof Access Permit MO&I Standard System Control Measures 24.0, 30.0
Other Fall Prevention Strategies | Falls from a height | H16 | • For all tasks 2.0 metres and over, identified as having potential for persons to fall. • Risk Assessment to identify the most appropriate fall prevention method for the location specific task, including 'fall restraint' & 'travel restraint' utilising the Hierarchy of Control. • Emergency Rescue Plan (ERP) incorporating a Retrieval Plan developed | Administration | • Task personnel are involved and trained in the location/task specific JSEA (or equivalent) & ERP; • Task personnel have attended recognised Fall Equipment training to "Work Safely at Height" • Include potential of falling objects and hot material from overhead Hot Works in JSEA • Correct installation & use of appropriate fall arrest equipment identified above | • JSEA (or equivalent) & ERP with Retrieval Plan for specific task/location • Statement of Attainment - Work Safely at Height • Task personnel have Statement of Attainment - Work Safely at Height | M9 | Asset Manager, Facility Management team, Service Providers
Industrial rope access | Falls from height/ falling objects | H20 | • All working at height equipment to be installed and maintained in accordance with manufacturers recommendations. •Engage appropriately qualified service providers. •All roof access to be controlled. •Rope access permit to be issued prior to commencing work. | Administration | • Service Provider to undertake CMS process • Appropriate permit to be in place. • Roof Access Management Plan to be adhered to • JSEA (or equivalent) signed by work crew, for all external tasks to establish effective means of preventing falling objects and preventing injury to personnel. • Certified anchor points. | • Routinely check roof access during property inspections. • On-site observation. • Industrial Rope Access permit • Fall restraint equipment register. • Record of inspection by a competent person at maximum 6 month intervals for safety harness and max 3 months for wire ropes or other fall arrest equipment. • Anchor point(s) certified prior to use or at max. 12 month intervals. • Training in the use of fall arrest equipment verified | M9 | Asset Manager, Facility Management team, Service Providers
Building Maintenance Unit (BMU) Level 16 | Falls from height/ falling objects | H20 | • Designed in accordance with Australian Standards • Operated by competent persons in accordance with Australian Standards • BMU Platform must have sufficient, clearly designated safety harness anchorage points designed to withstand forces caused by a fall of any person located anywhere on the platform. • BMU Permit issued prior to commencing works. | Administration | • Service Provider to undertake CMS process • Appropriate permit to be in place. • JSEA (or equivalent) signed by work crew, for all external tasks to establish effective means of preventing falling objects and preventing injury to personnel. • Certified anchor points. • Registration of BMU. | • Routinely check roof access during property inspections. • On-site observation. • BMU permit • Preoperational checks to be completed before each use (BMU to be taken out of service if faults found). • BMU Operation Log is to be completed and verified before each use. • Record of inspection by a competent person at maximum 3 month intervals. • Registration of BMU. • Anchor point(s) certified prior to use or at max. 12 month intervals. • Record of training in BMU for operators. • Record of Working at Heights training for operators |  | Asset Manager, Facility Management team, Service Providers
Roof access | Falls from height/ falling objects | H20 | • No work within 3 metres of the edge. • If access to edge of roof is required (less than 3 meters) fall arrest is required. • Fall arrest to be tested and in date • All roof access to be controlled through a master key. • Roof access permit required for all roof access. | Administration | • Fall prevention strategy determined. • Scaffold or guardrail or other edge barrier provided. • Fall restraint system for flat roofs for work within 3 metres of the edge where the potential fall height is 3 metres or more. • Safety mesh installed below roof sheet. | • Handover certificate for scaffold or guardrail. • Records of inspection at max. 30 day intervals. • On-site observation. • Roof Access permit • Fall restraint equipment register. • Record of inspection by a competent person at maximum 6 month intervals for safety harness and max 3 months for wire ropes or other fall arrest equipment. • Anchor point(s) certified prior to use or at max. 12 month intervals. • Training in the use of fall arrest equipment verified. | M9 | Asset Manager, Facility Management team, Service Providers
Ladders | Falls from height/ falling objects | H16 | • Platform ladders to be used. If platform ladder cannot be used a risk assessment is to be completed. • All ladders to have an annual inspection and have a Mirvac compliance sticker • Restricted use of ladders, especially near open penetrations, edges, stairs or balconies • No climbing above 3rd highest rung, use 3 points of contact and chest to remain within stiles of ladder | Engineering | • Visual inspection of ladders • Ladder rated for industrial use (120 kg max), minimum 1.2 metres and in good condition. • Where repeated access to heights of 2 metres or more is required, an elevated work platform, (e.g. mobile scaffold or other) is used instead of a ladder, or handrail erected where ladder near an edge | • "Inspection before each use" included as Control Measure in JSEA for task • Included in Induction topics • On-site observation | M10 | Asset Manager, Facility Management team, Service Providers
Hoist (Personnel) Hoist (Personnel & Materials) | Falls from height/ falling objects | H22 | • Hoist working as designed including bells, limit switches, SWL displayed and moving parts guarded • Hoist operator competent • For personnel hoist, communication system functional • People not underneath areas where objects could fall | Engineering | • Handover certificate provided • Maintenance of hoist carried out as per manufacturer's recommendations • Inspection of hoist carried out (including daily log book) • Operator licenced (specific for materials or people required) • Maintenance of communication system is carried out as per manufacturer's requirements • Exclusion zone in place with a spotter (where required) maintained • Areas around hoist penetration meshed/guarded on all sides to a minimum height of 2.5 metres on each floor | • Records of certificates • Records of maintenance • On-site observation • Records of competency | H14 | Asset Manager, Facility Management team, Service Providers
Penetrations including ducts and risers | Falls from height/ falling objects | H16 | • Penetrations greater than 200 x 200mm are covered or provided with edge protection | Engineering | • Minimum 19mm plywood to cover penetrations • Covers are fixed with dyna bolts or similar to prevent unauthorised removal/tampering • Covers are capable of withstanding expected loads from people, plant and equipment or materials • Fall prevention strategy determined for work around ducts or risers • Use of safety harness to be in fall restraint mode for work around ducts or risers • Anchor point to be adequately load bearing | • On-site observation • Training in the use of fall arrest equipment verified. | M10 | Asset Manager, Facility Management team, Service Providers
WORK OVER or NEAR WATER
Where construction work is required to be carried out over or near water where handrail/barricade is not practicable, and within 1 metre of the water's edge | Injuries to people, damage to property and the environment | H16 | • Hand rails & platforms or equivalent fall protection erected where potential of fall into water exists • Equipment, plant, materials is not placed within 1 metre of water's edge. • Appropriate location specific methods implemented to prevent people falling or slipping into the water | Engineering | • Daily inspection of water's edge & fall protection completed by competent person • Fall restraint equipment installed (where applicable). • Personal Flotation Device (PFD) correctly worn by personnel. • Depth of water indicated, lifebuoys with retrieval ropes attached where depth exceeds 1.5 metres | • Records of inspection • On-site observation | M10 | Asset Manager, Facility Management team, Service Providers
UNDERGROUND STORAGE TANKS
Underground storage tanks (UST’s) Basement level 6 | Soil and Groundwater contamination, confined space (see confined space above) | H20 | • Regular inspections and testing. in accordance with AS4897, State Legislation, LG Legislation.. • Install safety and identification signage. • Dangerous Goods licence if quantities exceed the limit | Engineering | • Implement Environmental Management Plan as per EPA requirements. • Implementation of Signage and storage requirements. | • Regular inspections and testing. | M6 | Asset Manager, Facility Management team, Service Providers | "NSW: Work Health and Safety Act 2011 (NSW) Work Health and Safety Regulation 2017 (NSW) Qld: Work Health and Safety Act 2011 (Qld) Work Health and Safety Regulation 2011 (Qld) ACT: Work Health and Safety Act 2011 (ACT) Work Health and Safety Regulation 2011 (ACT) WHS Act 2011 (s)19-21 Duties of PCBUs AS4482.1:2005 Code of Practice" EPA UPSS Regulation 2019
Above ground fuel storage tank (day tanks levels 16, 5 & basement 6) | Soil and Groundwater contamination, confined space (see confined space above) |  | • Regular inspections and testing in accordance with AS4897, State Legislation, LG Legislation. • Install safety and identification signage. • Dangerous Goods licence if quantities exceed the limit • Ensure bunding is present and would hold 110% volume of the tank capacity. • Ensure fill point areas have a secondary containment system and spill kits provided | Engineering | • Implementation of UPSS & APSS Signage and storage requirements. | • Regular inspections and testing in accordance with AS4897, State Legislation, LG Legislation. |  | Asset Manager, Facility Management team, Service Providers
Under Petroleum Storage System (UPSS) Basement 6 | Soil and Groundwater contamination, confined space (see confined space above) | H20 | • Regular inspections and testing. • Install safety and identification signage. • Dangerous Goods licence if quantities exceed the limit | Engineering | • Implement Environmental Management Plan as per EPA requirements. • Implementation of Signage and storage requirements. | • Regular inspections and testing in accordance with AS4897, State Legislation, LG Legislation.. | M6 | Asset Manager, Facility Management team, Service Providers
VISITORS
Visitors | Injuries to visitors | H20 | • ALL visitors to be escorted while on the premises. • Relevant safety concerns and issues to be advised to visitors by escorting agent. NB: Visitors who frequent (more than once) site must be inducted. | Engineering | • All visitors to sign in and out when entering and exiting the premises. | • FM and HSE to regularly review CMS for compliance. | M6 | Asset Manager, Facility Management team, Service Providers | WHS Act 2011 (s)20 Further Duties of PCBUs WHS Regulations 2011 Chapter 3- General Risk & Workplace management MO&I Standard System Control Measures
ENVIRONMENTAL ASPECTS
AIR QUALITY
Indoor and outdoor air quality | Adverse reactions by tenant, public and employees to chemicals, particles and/or substances in the air | H16 | • Minimise dust released by disturbance of soil and/or gaseous emissions from operation of plant and equipment or vehicles. • Provide clean, healthy, fresh air to facility at all times. • Ensure adequate ventilation. • Ensure recommended chemicals and treatments are used in the correct quantities at all times. | Engineering | • Testing for bacteria, CO’s, temp and humidity on an annual basis in accordance with relevant AS. Reports reviewed for any out of parameters levels which require corrective action and the records to be kept on file. • Service provider engaged to carry out testing must provide written report which FM is to review for out of parameter levels, addressing corrective action where required. • Manufacturers recommendations for safe use of products - Safety Data Sheets (SDS) and equipment to be adhered to for processes within buildings that may affect air quality i.e. dry cleaning, generators etc. • Plant inspected on arrival to site. • Daily pre-start completed. • Inspection and maintenance as per manufacturer's requirements. • Minimise stockpile heights. • Stabilise long term stockpiles e.g. grass/ hyrdomulch | • FM to ensure annual testing of IAQ, or at more frequent intervals if deemed necessary. • Monthly testing of water system quality. • Water treatment service Provider to be regularly monitored to ensure the Cooling Tower Manual compliance is maintained and completed as required. • On-site observation • Maintenance records available | M10 | Asset Manager, Facility Management team, Service Providers | WHS Regulations 2011 (s)40 – 41 General Working Environment. (s)49 – 52 Managing risks from airborne contaminants & Hazardous Atmospheres AS3666-1995 Air handling and water systems of buildings - Microbial control AS1668.2-1991 Mechanical ventilation for acceptable indoor air quality AS1324-1996 Air filters for use in general ventilation and air-conditioning MO&I E&O Procedure- Indoor Air Quality MO&I Standard System Control Measures 3.0, 4.0
CONTAMINATED SOIL
Acid Sulphate or other | Damage to the environment | H16 | • Appropriate location specific methods implemented to avoid spread of contaminated soils and the potential of leachate entering sensitive areas | Engineering | • Survey and history of land prior to works starting • Soil test to be carried out by NATA certified lab (for tests being used) • Treatment processes not undertaken within 50 metres of a water source. • Acid sulphate soils transported to an appropriate treatment area. • The entire ASS stockpile must be bunded to prevent escape of leachate. • Obtain fill materials from certified source Samples of imported fill to be tested • Disposal off site instead of site remediation | • Records of survey and historical data • On-site observation • Soil test records • Records of certificates • Records of tested samples • Records retained of licenced transport and disposal/receipt of waste to EPA Licensed facility | M10 | Asset Manager, Facility Management team, Service Providers
RESOURCE MANAGEMENT
Potable Water - Level 16 | Depletion of non-renewable resources | M11 | • Identify opportunities to reduce potable water consumption in facilities where Mirvac Facility Management have operational control. • Deliver on the Mirvac 'This Changes Everything' strategy to implement a 5% reduction in potable water intensity by FY23. | Administration | • Monitor and report on building potable water consumption. • Perform annual NABERS Water ratings to benchmark performance. • Investigate new water efficiency technologies. | • Monitor building daily usage profiles generated from smart meter data. • Perform a comparison review of monthly water consumption generated from smart meter data. • Review historical quarterly water consumption data from invoices and meter data. • Review and analyse annual NGERS data. | L3 | Asset Manager, Facility Management team, Service Providers
Energy | Depletion of non-renewable resources Emissions of Greenhouse Gases | M11 | • Identify opportunities to reduce energy consumption and Greenhouse emissions in facilities where Mirvac Facility Management have operational control. • Deliver on the Mirvac 'This Changes Everything' strategy to implement a 5% reduction in carbon intensity by FY21. | Administration | • Monitor and report on building energy consumption and Greenhouse emissions • Perform annual NABERS Energy ratings to benchmark performance. • Investigate new energy and carbon efficiency technologies. | • Monitor building daily usage profiles generated from smart meter data. • Perform a comparison review of monthly water consumption generated from smart meter data. • Review historical quarterly water consumption data from invoices and meter data. • Review and analyse annual NGERS data. | L3 | Asset Manager, Facility Management team, Service Providers
SPILLS OR DISCHARGE CAUSING CONTAMINATION
Storage and Handling of Hazardous Substances and/or Dangerous Goods | Spills or discharge causing contamination Injury/Illness of Member of Public, Contractor or Worker | H17 | • Substances/goods stored in accordance with Safety Data Sheet (SDS)/(MSDS) • Storage area bunded and away from drainage inlets or other sensitive areas. • Substances/goods stored and handled in accordance with SDS (MSDS). • Appropriate PPE made available. • Users trained in correct use of substance. | Engineering | • Signage and emergency response equipment available relevant to the class of substance/good stored. • Nominated personnel trained in spill response. • Bunding designed to meet required 110% of largest individual container. • No fuel storage within 50 metres of a water body. • Spill Kit available. • Minor quantities only stored which do not require licencing. • Pressurised gas cylinders/bottles secured from toppling and stored in ventilated area with restricted access. | • Spill Kit stocked • Records of spill response training available • On-site observation • Drainage outlet to bunding locked | M10 | Asset Manager, Facility Management team, Service Providers
WASTE
Recycles • general and prescribed waste (solid & liquid) | Non-compliance and breaches of EPA regulations | H16 | • Waste is minimised & stored securely • Waste generated is collected and recycled in accordance to the Waste Management Hierarchy. • Waste is managed and stored securely. Waste material is disposed of by reputable contractors in accordance with legislative requirements. • Deliver on the Mirvac 'This Changes Everything' strategy to implement a 85% recycling rate across the Investment portfolio by FY23. | Engineering | • Waste storage facilities established according to estimated volume including paint tanks and recycling bins/skips for all streams. • Waste sorted on site or at the waste depot. • Transporter and receiver of waste are EPA Licensed. • Waste transport certificate is obtained (this verifies waste was disposed of in the correct facility) e.g., Adhesives (excluding solid inert polymeric materials), Lime sludges or slurries, Paint sludges and residues, Pesticides (including herbicides & fungicides), Timber preservative residues. • Mirvac require waste contractors to only utilise appropriately licenced facilities and to declare these facilities to Mirvac with the licencing details. • Mirvac investigate and implement applicable waste management and recycling technologies. • Waste Management Plans for each asset where Mirvac Retail manage waste services. • Perform waste audits to identify waste minimisation and recycling opportunities. | • Monthly waste records including quantities diverted from landfill to recycling • Records of licences. • Review of service provider JSEA for works which constitute a “material risk to environment/ generate significant wastes streams” prior to commencement of work. • Records of certificates of disposal from waste removal contractor which are forwarded to the Sustainability data collection point. • Hold regular meetings with waste contractors. • Review historical quarterly water consumption data from invoices and meter data. • Review and analyse annual NGERS data. | L5 | Asset Manager, Facility Management team, Service Providers | Environment Protection Act 1997 Mirvac Group Hazardous Waste Disposal Procedure Mirvac Group Products and Hazardous Substances Register Mirvac Group Hazardous Substance Risk Assessment MO&I Standard System Control Measures 57.0
Note on A4: Amanda Reid: (Potential cause of injury/illness or cause of damage to the environment – as identified on Hazard/Aspect Worksheet)
Note on B4: Amanda Reid: (What could happen)
Note on D4: Amanda Reid: (According to Hierarchy of Controls, Elimination of the hazard/aspect is our primary objective)
Note on F4: Amanda Reid: (What we need to do to ensure the Controls are implemented, effective & operational)
Note on G4: Amanda Reid: (What tools are used to monitor the critical controls and critical activities for effectiveness)
Note on J4: Amanda Reid: (Statutory requirements from Commonwealth or State Government, Council Ordinances, Regulations, By-laws, EPA, Australian Standards and Codes of Practice, relevant to each Critical Control)
Note on D80: Amanda Reid: What is the O&I version Melanie Jones: Confirmed with Al Lutzke no specific O&I document is in place, we would reference AS.
Note on D84: Amanda Reid: reference stop work temp / humidity levels Melanie Jones: *SafeWork NSW* WHS Regulations don't specify a specific temperature because exposure to illnesses is dependent on a number of factors.
Note on J109: Amanda Reid: Check if referencing correct mmr
Note on D140: Amanda Reid: populate with controls

## Sheet1 (hidden)
L1
L2
L3
L4
L5
M6
M7
M8
M9
M10
M11
M12
M13
H14
H15
H16
H17
H18
H19
H20
H21
H22
E23
E24
E25

## MAJOR HSE RISKS
Asset Name: 255 Elizabeth Street, Sydney (LA2005)
Date: 12/02/2024
Prepared By: Adrian Everingham
Note: Insert the top 5 HSE risks for your Asset and or any unusual HSE risk
Risk Hierarchy: E = Extreme, H = High, M = Medium, L = Low
Description Provide a description of the identified task or operation | Upcoming, active or closed | Hazard/Risk | Untreated Risk | Risk Mitigation Strategy Provide a summary of the risk mitigation strategy action | Monitoring Activities Provide a summary of how the risk mitigation strategy action will be monitored | Residual Risk | Person / Team Member to Monitor | Changes/ Reviews | Comments Provide any other general comments as required
EV - LiB thermal Runaway Hazards | Active | Access for the Fire Brigade to location of EV Chargers & Awarness Lack of Ventilation & Emergency Egress Proximity to essential services & flammable or explosive items Fire suppression systems EV Charger equipment maintenance, commissioning and system safety capabilities | H (18) | Ensuring there is a clear pathway to treat vehicle in the event of incident All Emergency access & egress points must be clear of obstructions at all times. Adequate ventilation mechanical and/or natural is in place At the time of design and construction the property complied with relevant AS, BCA or construction guidance - (Ordinance 70 if prior to AS). Identify the location of any essential services, gas lines, MSR’s, FCR’s, fuel storage, flammable materials & chemical storage prior to installation. No essential services to be within 15m of the closest EV car charging bay Adequate water supply availability Fire Sprinkler system in place / Fire Hydrant system in place / Fire Hose Reels in place / Fire Extinguishers in place Ensure high quality equipment is installed and that it has highest level of safety built in to the system (see additional tab - EV Charger Equipment Assessment) EV charger system reporting, analysis and alarming system capability Installation and commissioning certification obtained prior to energisation Bollards and wheel stops in front of charging equipment | Include EV inspection regime for security & onsite operations teams FCR36 - Inspection of EV chargers Quarterly contractor engagement confirming maintenance task have been completed Records of maintenance and Essential Services certification Records of Workplace inspections. | L (4) | Mirvac Workplace Managers, Service Providers | On going
Major HSE Risks from the Risk Register